GOVERNMENT OF ANDHRA PRADESH

ABSTRACT

Municipal Administration & Urban Development Department – Drinking Water Supply – Strengthening of Water Quality Monitoring and Surveillance in Urban Local Bodies – State Action Plan and Standard Operating Procedure (SOP) for Drinking Water Quality Monitoring, Surveillance and Public Disclosure – Orders – Issued.

==================================================

MUNICIPAL ADMINISTRATION & URBAN DEVELOPMENT (K) DEPARTMENT

G.O.MS.No. 66							Dated: 25-03-2026

Read the following:-

1.	Memo No.2980221/K/2025, MA&UD Department, dated 26.02.2026.

2.	Proposal from Engineer-in-Chief, Public Health & Municipal Engineering Department and Commissioner & Director of Municipal Administration, vide e-file bearing C.No:3115328, Dt. 12.03.2026.

&&&

ORDER:

In the reference 1st read above, Government have issued consolidated directions to all Municipal Commissioners of the Urban Local Bodies in the State for the prevention and containment of water-borne and vector-borne diseases through a Statewide Special Drive for ensuring safe drinking water supply, rectification of pipeline leakages, and strengthening of public health safeguards.

2.	Urban Local Bodies are responsible for ensuring the supply of safe and potable drinking water to the public, which is a critical public health function. Recent incidents of diarrhoeal and gastroenteritis outbreaks reported in certain urban areas have highlighted the need to strengthen water quality monitoring, improve surveillance of drinking water supply systems, and establish timely response mechanisms to prevent contamination.

3.	Government has taken serious note of the systemic deficiencies observed in water supply management in certain Urban Local Bodies, including pipeline leakages, inadequate chlorination practices, and lack of robust water quality monitoring mechanisms. Ensuring safe drinking water supply and preventing waterborne diseases is of paramount importance to safeguard public health.

4.	In order to institutionalize a robust, technology-enabled and accountable monitoring, testing and response framework and based on the proposal submitted by the Engineer-in-Chief, Public Health & Municipal Engineering Department and Commissioner & Director of Municipal Administration vide reference 2nd read above, Government have prepared a comprehensive State Action Plan and Standard Operating Procedure (SOP) for Drinking Water Quality Monitoring, Surveillance and Public Disclosure in Urban Local Bodies, which, inter alia, provides for:

- Establishment of a multi-layer water quality monitoring system, including mobile water testing laboratories, handheld testing devices and strengthened in-house laboratories.

(P.T.O)

:: 2 ::

- Adoption of risk-based vulnerability mapping and GIS-integrated sampling framework to ensure scientific and spatially distributed water quality surveillance.

- Mandatory residual chlorine monitoring across all levels of the drinking water supply system as a non-negotiable safety parameter.

- Implementation of structured and time-bound contamination detection, response and incident reporting protocols.

- Provision for enhanced surveillance and increased sampling frequency during waterborne disease outbreaks, disasters and emergency situations.

- Prescribing comprehensive testing protocols covering physical, chemical, bacteriological and other parameters in accordance with BIS IS 10500:2012 standards.

- Ensuring periodic calibration and maintenance of water quality testing equipment to maintain accuracy and reliability of test results.

- Strengthening data-driven governance through real-time reporting and monitoring via the APCMMS platform.

- Establishing regulatory and monitoring framework for private RO plants and extending oversight to food establishments including street vendors and eateries.

- Promoting public awareness along with enforcement measures, including action against illegal suction connections and violations affecting water safety.

- Ensuring transparency through public disclosure of water quality information

5.	Government, after careful examination of the matter, hereby approves and orders the implementation of the State Action Plan and Standard Operating Procedure (SOP) for Drinking Water Quality Monitoring, Surveillance and Public Disclosure in Urban Local Bodies, appended to this order as Annexure.

6.	All Municipal Commissioners and Municipal Engineers (all cadres) shall strictly implement the provisions contained in the State Action Plan and SOP, including GIS- based sampling, risk-based monitoring, mandatory testing protocols, contamination response mechanisms, enforcement measures and public disclosure requirements, and ensure full compliance in all Urban Local Bodies.

7.	The Engineer-in-Chief, Public Health & Municipal Engineering Department shall provide necessary technical guidance to Urban Local Bodies, including standardization of testing protocols, calibration of equipment, strengthening of laboratory infrastructure, and improvement of water treatment and distribution systems.

8.	The Commissioner & Director of Municipal Administration (C&DMA) shall monitor the implementation of the Action Plan across all Urban Local Bodies through the APCMMS platform and State-level dashboards, including tracking of sampling coverage, incident response timelines, data reporting compliance and performance indicators.

[Contd...P.3]

:: 3 ::

9.	Any negligence in ensuring safe drinking water supply will be viewed seriously and responsibility shall be fixed accordingly.

10.	This order shall come into force with immediate effect.

(BY ORDER AND IN THE NAME OF THE GOVERNOR OF ANDHRA PRADESH)

S SURESH KUMAR

PRINCIPAL SECRETARY TO GOVERNMENT

To:

All Municipal Commissioners in the State (through C&DMA)

All Municipal Engineers (all cadres) in the Urban Local Bodies (through ENC -PH&MED)

Copy to:-

The Secretary to Government, HM&FW Department, A.P Secretariat for  information The Commissioner & Director of Municipal Administration for information and necessary action.

The Engineer-in-Chief, Public Health & Municipal Engineering Department for information and necessary action.

The P.S to Hon’ble Minister for MA&UD Department.

The P.S to Principal Secretary to Government, MA&UD Department.

Sf/Sc.

// FORWARDED :: BY ORDER //

SECTION OFFICER

Annexure to G.O.Ms.No.  , MA&UD(K) Dept., dated:25.03.2026.

STATE ACTION PLAN AND STANDARD OPERATING PROCEDURE (SOP)FOR DRINKING WATER QUALITY TESTING, SURVEILLANCEAND PUBLIC DISCLOSURE

&&&

Part-1: State action plan for drinking water quality monitoring

In order to ensure the Quality of drinking water supplied by ULBs and strengthen public health safety standards to ensure Zero water contamination and disease outbreaks, a structured monitoring mechanism for drinking water quality is required across all Urban Local Bodies. This State Action Plan provides the framework for establishing a multi-layer water quality monitoring system, including strengthening of testing infrastructure, field-level testing, and mandatory residual chlorine monitoring across the Municipal water supply system. The Action Plan aims to enable early detection of contamination, timely corrective action, and improved transparency in water quality management, thereby ensuring that drinking water supplied to citizens complies with prescribed safety standards.

- Objectives

- Ensure safe drinking water supply complying with BIS IS 10500:2012 standards.

- Establish multi-layer water quality monitoring system.

- Prevent waterborne disease outbreaks.

- Enable real-time monitoring and corrective action through APCMMS portal.

- Strengthen field level testing capacity in all ULBs.

- Proactive disclosure of water quality test results to public through APCMMS and RTGS AWARE

- Water Quality Monitoring Infrastructure

  - Handheld Residual Chlorine Testing Devices

- One Handheld RC Testing Device to be issued to each Ward Amenities Secretary

- These handheld devices constitute the first layer of water quality monitoring and the sampling coordinates and resultsto be propagated to the APCMMS dashboard.

  - Handheld Digital Water Testing Devices

- One Handheld Digital Water Testing Device per ULB to be issued to Municipal Engineer (Highest Cadre Engineer).

- Functions:

    - For Regular Field level rapid testing for:

      - Residual Chlorine

      - pH

      - Turbidity

      - TDS

  - For Daily monitoring at

    - Service reservoirs

    - Distribution points

    - Tail end locations

    - For Emergency Field level rapid testing for:

      - Nitrites & other chemical parameters

  - For need based emergency monitoring at

    - Sampling locations where contamination suspected

2.3 In-house Water Testing Laboratories

- All Water Testing Laboratories existing at the Water Treatment Plants to be upgraded for IoT compliance duly providing necessary equipment, instrumentation and staff.

- Functions:

    - Multi-parameter physical & chemical analysis

    - Bacteriological testing

- Daily monitoring at

    - Raw water source point

    - WTP outlet

2.4 Mobile Water Testing Laboratories ( on PPP/ service outsourcing model)

- One Mobile Water Testing Laboratory per erstwhile district (13 Nos.)

- Coverage: All ULBs within the district.

- Functions:

  - Multi-parameter chemical analysis

  - Bacteriological testing

  - Emergency outbreak investigation

  - Random sampling in distribution network

Mobile labs shall act as rapid response units for contamination detection.

## 3. Risk-Based Vulnerability Mapping and Differential Sampling Strategy

a. In order to strengthen preventive surveillance, all Urban Local Bodies shall adopt a Risk-Based Vulnerability Mapping approach for drinking water distribution systems.

b. Each ULB shall divide its jurisdiction into “Water Quality Vulnerability Zones” based on the following parameters:

- Age and material condition of pipelines

- History of waterborne disease outbreaks

- Frequency of past contamination incidents

- Low pressure / tail-end supply areas

- Areas with known leakages or cross-connections

- High-density and vulnerable population clusters

c. Based on the above assessment, zones shall be classified as:

- High-Risk Zones

- Moderate-Risk Zones

- Low-Risk Zones

d. Sampling frequency shall be determined based on risk category, overriding population-based norms where necessary:

- High-Risk Zones – Increased sampling frequency (at least 2–3 times the standard frequency)

- Moderate-Risk Zones – Standard prescribed frequency

- Low-Risk Zones – Minimum prescribed frequency

e. Vulnerability maps shall be:

- Digitally integrated with the APCMMS portal

- Updated annually or after any major contamination incident

f. This approach shall ensure targeted surveillance, early detection, and efficient resource utilization.

4. Mandatory Residual Chlorine (RC) Monitoring

4.1. Residual Chlorine testing shall be treated as Non-Negotiable Safety Parameter.

Minimum limits:

| Location | Minimum RC |
| --- | --- |
| WTP Outlet | 0.5 ppm |
| Reservoir Outlet | 0.2 ppm |
| Consumer End | 0.2 ppm |

4.2. Cleaning of ELSRs – Elevated Level Service Reservoir (Overhead water storage tank used for distribution of treated drinking water):

- Water supply staff of ULBs must carry-out periodical maintenance and cleaningincluding cleaning of ELSRs at monthly intervals involving SHG group and local public.

If RC = 0 → Water shall be treated as unsafe.

4.3. Residual Chlorine Testing Protocol

- RC testing shall be conducted daily in all ULBs.

- Test locations include:

  - WTP outlet

  - GLSRs / ELSRs

  - Distribution network

  - Tail end points

  - Public stand posts

  - Random consumer points

- All test results shall be uploaded in APCMMS portal daily.

- RC tests shall be conducted in schools, Colleges, Anganwadi centres and Welfare Hostels where Drinking water supply is through ULBs on daily basis and registers should be maintained.

- All private schools, hostels, paying guest (PG) accommodations and other private establishments shall ensure that drinking water either supplied by ULB or from any other source, within their premises is tested for physical, chemical and bacteriological parameters once every month through IPM Laboratories or NABL accredited laboratories at their own cost. The test reports shall be maintained at the premises and produced for inspection by Urban Local Body officials whenever required. In case of non-compliance, appropriate action may be taken by the Urban Local Body as per applicable regulations.

- In addition, all food establishments including street vendors, tiffin centres, eateries, restaurants and other food handling units shall ensure that drinking water used for consumption and food preparation is tested periodically through approved laboratories.

- The test reports shall be maintained and produced for inspection by Urban Local Body officials. Non-compliance shall attract action as per applicable municipal and public health regulations.

5. Contamination Detection and Response Protocol

A structured response mechanism shall be followed by Urban Local Bodies to ensure early detection of contamination and prompt corrective action in the drinking water supply system.

## Case 1: Residual Chlorine (RC) Failure

If the Residual Chlorine level at any testing location is found to be below the prescribed limit but within a deviation of 0.2 ppm, the following actions shall be taken:

- The concerned Municipal Engineer or field officer shall immediately verify the test result using a handheld digital testing device.

- A Nitrite Test shall be conducted within three hours of detection.

- An alert shall be generated to the Mobile Water Testing Laboratory for further investigation.

- Chlorination levels at the Water Treatment Plant and reservoirs shall be checked and corrective dosing shall be ensured.

## Case 2: Nitrite test Failure or Suspicion of Contamination

If the nitrite test indicates contamination or if contamination is suspected:

- The Mobile Water Testing Laboratory shall reach the affected location within three hours.

- Detailed bacteriological testing shall be carried out.

- The distribution system in the affected area shall be inspected to identify possible sources of contamination, including:

  - Pipeline leakages

  - Cross connections with drains

  - Low pressure zones

  - Illegal suction connections.

## Case 3: Bacteriological Contamination

If E.coli or bacteriological contamination is confirmed:

- The affected storage reservoir and distribution zone shall be immediately identified.

- Water supply from the contaminated reservoir shall be temporarily stopped.

- Citizens shall be advised to discard stored drinking water collected during the contamination period.

- Safe drinking water supply shall be arranged through water tankers until normal supply is restored.

- The following corrective measures shall be undertaken:

  - Super chlorination of reservoirs

  - Flushing of distribution pipelines

  - Repair of pipeline leakages

  - Removal of cross connections with drains

- The affected reservoir shall be cleaned and disinfected before restoring supply.

Water supply shall be restored only after laboratory tests confirm that water quality meets the prescribed safety standards.

6. IEC Activities and  Enforcement

# Urban Local Bodies shall undertake Information, Education and Communication (IEC) activities along with enforcement measures to ensure safe water practices.

# 6.1. IEC activates and stakeholder involvement

# All stakeholders shall be educated about the importance of safe drinking water and the steps ( precautions) to be taken to avoid contamination of water.

- Avoid drawing water during non-supply hours

- Prevent illegal suction pumps and direct connections to pipelines

- Maintain hygiene in household and commercial water storage systems,

- Ensure periodic cleaning of overhead tanks and storage containers ( barrels/ bins)

- Prompt reporting of leakages and contamination incidents- change in water colour, smell, turbidity etc.

6.2. Enforcement measures:

- ULBs shall conduct special enforcement drives to identify and remove illegal suction pumps, leakages etc.

- Penalties shall be imposed as per municipal regulations for violations affecting the integrity of the water supply system.

- Periodic inspection of water storage practices in bulk consumers and commercial establishments shall be undertaken.

Figure: Residual Chlorine Monitoring and Contamination Response Framework

Part – 2: Standard Operating Procedure for waterquality testing

# 1. Water Quality Testing Protocol

# All ULBs shall strictly adhere to the following testing protocol.

| S. No. | Type of Test | Frequency of Testing | Location of Sample Collection | Testing of sample |
| --- | --- | --- | --- | --- |
| - Physical: 6 No. of Tests |  |  |  |  |
| 1 | - Temperature - Turbidity - Colour - Taste - Odour - Total Dissolved Solids - Conductivity | Daily | - Raw Water from Off-Take Chamber, Intake Well etc. - Stilling Chamber of the WTP - Sedimentation Tank after clarifier - Filtered Water at WTP - Clear Water Reservoirs | In-House |
|  |  | Monthly | Ground Water (Tube Well/ Bore Wells/ Hand Bores/ Infiltration Wells) | In-House |
| - Chemical: - 12 No. of Tests |  |  |  |  |
| 2 | - Residual Chlorine | Daily | - Clear Water Sump - ELSRs - Distribution System - HSCs - Ground Water (Tube Well/ Bore Wells/ Hand Bores/ Infiltration Wells) | In-House |
| 3 | - pH - H2S vial test | Daily | 1. Distribution System 2.HSCs 3.Ground Water (Tube Well/ Bore Wells/ Hand Bores/ Infiltration Wells) | In-House |
| 4 | - Total Alkalinity - Chlorides - Dissolved Oxygen - Total Hardness - Iron - Fluorides - Nitrates - Magnesium - Total Nitrogen (Ammonia) | 15 Days | 1.Raw Water 2. Clear Water Sump 3. ELSRs 4. Distribution System - HSCs | - In-House and/ or - IPM Lab and/ or - RWS Lab and/ or - APPCB LAB and/ or - NABL accredited LAB (3rd Party) |
|  |  | Quarterly | Ground Water (Tube Well/ Bore Wells/ Hand Bores/ Infiltration Wells) |  |
| - Bacteriological: 1 No. of Test |  |  |  |  |
| 5 | Escherichia Coli (E.Coli) | Weekly | - Raw Water - Filtered Water at WTP - Clear Water Sump - ELSRs - Distribution System | - IPM Lab and/ or - RWS Lab and/ or - APPCB Lab and/ or - NABL accredited Lab (3rd Party) |
|  |  | Quarterly | Ground Water (Tube Well/ Bore Wells/ Hand Bores/ Infiltration Wells) |  |
| - Heavy Metals: - 21 Nos. of Tests |  |  |  |  |
| 6 | - Calcium - Manganese - Copper - Zinc - Aluminium - Sulphates - Sulphide - Lead - Arsenic - Mercury - Selenium - Chromium - Cyanide - Nickel - Cadmium - Barium - Silver - Boron - Phenolics - Hydrocarbons - Chemical Oxygen Demand | Quarterly | - Raw Water - Clear Water Sump - ELSRs - Distribution System. - HSCs - Ground Water (Tube Well/ Bore Wells/ Hand Bores/ Infiltration Wells) | - IPM Lab and/ or - RWS Lab and/ or - APPCB LAB and/ or - NABL accredited LAB (3rd Party) |
| - Pesticides: - 14 No. of tests |  |  |  |  |
| 7 | Organo-Phosphates (9): - DDT - Chloroform - Endosulfan - Aldrin - Dieldrin - Butachlor - Methocychlor - Alachlor - Endrin Organo-Chlorides (5): - Methyl Parathion - Malathion - Chlorpyriphos - Ethion - Mono-crotophos | Quarterly | - Raw Water from Off-Take Chamber, Intake Well etc. - Clear Water Sump - ELSRs - Distribution System. - HScs - Ground Water (Tube Well/ Bore Wells/ Hand Bores/ Infiltration Wells) | - IPM Lab and/ or - RWS Lab and/ or - APPCB LAB and/ or - NABL accredited LAB (3rd Party) |

2. Sampling Procedure:

The Bureau of Indian Standards (BIS), in Indian Standard Specification IS 1622:1981 and IS 3025: Part I to Part 60 prescribed the sampling procedure for taking water samples for testing and the procedure of testing for various Physical, Chemical, Bacteriological, Heavy Metals and Pesticides etc. and the minimum no. of samples to be tested at each frequency of testing as follows, but not limited to.

| Sl. No. | Location of Sample collection | Minimum No. of samples to be tested |
| --- | --- | --- |
| 1 | Raw Water from Off-Take Chamber, Intake Well etc. | Not less than One Sample |
| 2 | Ground Water (Tube Well/ Bore Wells/ Hand Bores/ Infiltration Wells) | Not less than One sample for each Borewell/ Tube Well/ Infiltration Well |
| 3 | Stilling Chamber of the WTP | Not less than One sample |
| 4 | Sedimentation Tank after clarifier | Not less than One sample |
| 5 | Filtered Water at WTP | Not less than One sample |
| 5 | Clear Water Sump | Not less than One Sample |
| 6 | Clear Water Storage Reservoirs (ELSRs/ GLSRs) | Not less than One Sample for each Reservoir |
| 7 | Distribution System | Not less than One sample for every 5000 population |
| 8 | House Service Connections (HSCs) (Residual Chlorine test) | Not less than One Sample for every 500 HSCs issued |

2.1 GIS-Based Sampling and Spatial Coverage

  - All water sampling locations across the distribution system shall be geo-tagged and integrated with GIS-based maps within the APCMMS platform.

  - Each Urban Local Body shall prepare a daily sampling plan ensuring equitable spatial coverage across all wards and service zones.

  - Sampling shall be distributed in such a manner that the entire distribution network is covered over a defined cycle, avoiding repeated sampling from the same locations.

  - GIS-based monitoring shall be used to identify unserved or under-sampled areas and to optimize sampling strategies.

3. Distribution System Inspection

ULBs shall conduct special drives to identify contamination risks such as:

- Pipelines crossing open drains

- Leakages in distribution network

- Low pressure tail end areas

- Old pipeline stretches

- Drain water ingress

- Documentation of shifting of pipelines crossing the drains.

4. Mandatory Sanitary Inspection Protocol

a. A standardized Sanitary Inspection Mechanism shall be institutionalized across all ULBs.

b. Every instance of the following shall mandatorily trigger a Sanitary Inspection:

- Residual Chlorine (RC) failure below prescribed limits

- Nitrite failure

- Bacteriological contamination (E. coli / coliform)

- Repeated complaints of water quality issues

c. A Standard Sanitary Inspection Form (SSIF) shall be prescribed and digitized within APCMMS, capturing:

- Location and sample details

- Condition of pipelines (age, material, leakages)

- Proximity to drains/sewer lines

- Presence of cross-connections

- Evidence of illegal suction connections

- Reservoir hygiene and maintenance status

- Pressure conditions in the network

d. The inspection shall be completed:

- Within 24 hours of detection of failure

e. The findings shall:

- Be uploaded in APCMMS

- Include geo-tagged photographs

- Be linked to the specific incident under WSIRS

f. Corrective actions identified through inspection shall be:

- Time-bound

- Monitored till closure

## 5. Public Disclosure of Water Quality Information

In order to promote transparency and public confidence in the drinking water supply system, Urban Local Bodies shall ensure that water quality information is regularly disclosed in the public domain.

Urban Local Bodies shall ensure the following:

- Daily Residual Chlorine (RC) test results are uploaded on the APCMMS portal.

- Water quality dashboards are displayed on ULB websites and integrated with the State monitoring system.

- Key water quality information is displayed at:

  - Water storage reservoirs

  - Municipal offices

  - Ward secretariats

  - Public notice boards.

- The test results shall be shared with RTGS on a real time basis through an API for use in AWARE

In case of contamination or suspected outbreaks, public advisories shall be issued through public announcements, local media and digital communication platforms, advising citizens to take precautionary measures such as boiling water before consumption until safe supply is restored.

Part 3: Monitoring and Governance framework

1. Data Management & Reporting

1.a. All ULBs shall ensure:

- Daily RC test reporting

- Water quality test uploading in APCMMS portal

- Maintenance of registers:

  - RC test register

  - Water quality register

  - Bacteriological test register

1.b. Calibration and Maintenance of Testing Equipment

- All water quality testing equipment, including handheld devices and laboratory instruments, shall be calibrated at regular intervals, at least once every three months, through certified agencies.

- Calibration records shall be maintained at the Urban Local Body level and shall be subject to audit and verification.

- Any equipment found to be malfunctioning or deviating from standard readings shall be immediately withdrawn from use and rectified.

- Ensuring accuracy and reliability of testing equipment shall be the responsibility of the Municipal Engineer.

2. Institutional Responsibilities

  - Municipal Commissioner

- Overall responsibility for safe drinking water supply.

  - Municipal Engineer

- Water quality monitoring

- Field testing supervision

- Data uploading

  - Mobile Lab Team

- Random sampling

- Emergency outbreak investigation

d. Regional Directors and the office of the Commissioner & Director of Municipal Administration shall undertake district and state level monitoring.

3. Monitoring Mechanism

| Level | Responsibility |
| --- | --- |
| Ward Amenity Secretary / Assistant Engineer | Daily testing of RC at WTPs,ELSRs and Tail End distribution |
| Municipal Engineer | Daily monitoring |
| Municipal Commissioner | Daily monitoring |
| Regional Director | District review |
| C&DMA, Engineer-in-Chief | State monitoring |

4. Compliance

APCMMS shall provide a monthly performance dashboard indicating the highest and lowest performing ULBs, and any negligence in water quality monitoring shall invite strict disciplinary action.

S SURESH KUMAR

PRINCIPAL SECRETARY TO GOVERNMENT